Checkout - SWR BKR 2B - Primary Block

Safety Procedures

OFCI Equipment Checkout Safety Plan

- Pre-energization inspection is completed and the equipment is ready to be energized

- Perform ORM with all personnel involved and review procedure as well as backout plan. Identify muster point

- Verify appropriate safety zones and barricades are in place in accordance to our control scheme

- Area access control is in place

- Equipment signs - nameplate, name tag, arc-flash labels, and safety signage - are installed correctly

- Verify proper operation of test equipment

- Safe work conditions have been established and verified prior to energization

- Work with Vendor support team

| Equipment Tag Name | Equipment Manufacturer | Equipment Model |
| --- | --- | --- |
| RIC2_DC6_SWR_B1_BKR_2B | ABB | EMAX 4.2 |

| Section A - Analog Control Points |  |  |  |  |
| --- | --- | --- | --- | --- |
| Data Point | Field Value | SCADA Value | Values Match | Incident Report No. / Notes |
| Data/Amps_A |  |  |  |  |
| Data/Amps_Avg |  |  |  |  |
| Data/Amps_B |  |  |  |  |
| Data/Amps_C |  |  |  |  |
| Data/Amps_G |  |  |  |  |
| Data/Amps_N |  |  |  |  |
| Data/kVA |  |  |  |  |
| Data/kW |  |  |  |  |
| Data/kWh |  |  |  |  |
| Data/PF |  |  |  |  |
| Data/Pos |  |  |  |  |
| Data/Status |  |  |  |  |
| Data/Volts_AB |  |  |  |  |
| Data/Volts_AN |  |  |  |  |
| Data/Volts_BC |  |  |  |  |
| Data/Volts_BN |  |  |  |  |
| Data/Volts_CA |  |  |  |  |
| Data/Volts_CN |  |  |  |  |
| Data/Volts_LL_Avg |  |  |  |  |
| Data/Volts_LN_Avg |  |  |  |  |
| Section B - Digital Control Points |  |  |  |  |
| Data Point | Status Simulated / Command Sent | Status Verified in SCADA | Pass/ Fail | Incident Report No. / Notes |
| Data/CB_Position |  |  |  |  |
| Data/Comm_Fail |  |  |  |  |
| Data/Status_Changed |  |  |  |  |
| Section C - Alarm Points |  |  |  |  |
| Data Point | Status Simulated | Status Verified in SCADA | Pass/ Fail | Incident Report No. / Notes |
| Data/Breaker_Status_Alarm |  |  |  |  |
| Data/CB_NC |  |  |  |  |
| Data/CB_NO |  |  |  |  |
| Data/Percent_Load |  |  |  |  |
| Data/Tripped |  |  |  |  |
| Section D - Memory Points |  |  |  |  |
| Data Point | Status Simulated/ Command Sent or Field Value | Status Verified in SCADA or SCADA Value | Pass/ Fail or Values Match | Incident Report No./Notes |
| Data/Amp_Rating |  |  |  |  |
| Data/CB_Normal_State |  |  |  |  |
| Data/Feeds |  |  |  |  |
| Data/Nominal_Volts |  |  |  |  |

SCADA Evidence Screenshots

| Punchlist Items |  |  |  |  |
| --- | --- | --- | --- | --- |
| # | Description | Assign To | Status | Incident Report No. / Notes |
| 1 |  |  | Choose an item. |  |
| 2 |  |  | Choose an item. |  |
| 3 |  |  | Choose an item. |  |
| 4 |  |  | Choose an item. |  |
| 5 |  |  | Choose an item. |  |
| 6 |  |  | Choose an item. |  |

| M.C. Dean | Engineer | QC Representative |
| --- | --- | --- |
| Print Name: |  |  |
| Signature: |  |  |
| Date: |  |  |